## Configuration
Spectrex, Inc. | [6 empty] | Spreadsheet ID: FDC-4040-1.7
SharpEye Flame Detector Configuration Spreadsheet V1.7 |  |  |  | Config cannot be easily changed by the user
| Purchase Order Information |  |  | Detector Configuration Descriptions | [8 empty] | 4-20mA Default Settings
|  | Distributor Name: | Enter Name Here | Detector Type | LB- | Wiring Options | [7 empty] | 40/40I, M, R, U, UB |  |  | 40/40L,LB,L4,L4B
|  | Purchase Order #: | Enter P.O.# Here | I - IR3 | [9 empty] | Default | Special Request |  | Default | Special Request
|  | Order Date: | 2026-07-29 | M - Hydrogen + Hydrocarbon |  | Wiring |  | 4-20 | mA |  | Relays |  | Fault | 0mA | 0mA | Fault | 0mA | 0mA
|  | Current Detector Model #: | 40/40LB-112SF | R - Single IR |  | Options | RS-485 | Configuration | HART | Fault * | Aux./ACC | Alarm | Bit Fault | 2mA* |  | Bit Fault | 2mA*
|  | Quantity of Units: | 1 | L - UV/IR (without BIT) |  | 1 | Yes | Sink | None | NC | None | NO | Normal | 4mA |  | Normal | 4mA
|  |  |  | LB - UV/IR (with BIT) |  | 2 | Yes | Source | Yes | NC | None | NO,NC | Warning | 16mA |  | IR Detection | 8mA
|  |  |  | L4 - UV/IR ( IR at 4.5um without BIT) |  | 3 | Yes | Source | Yes | NO | None | NO,NC | Alarm | 20mA |  | UV Detection | 12mA
|  |  | 0% | L4B - UV/IR ( IR at 4.5um with BIT) |  | 4 | Yes | None | None | NC | NO | NO | * This staus is not applicable in 40/40U. |  |  | Warning | 16mA
|  |  |  | U - UV (without BIT) |  | 5 | Yes | None | None | NO | NO | NO |  |  |  | Alarm | 20mA
|  |  |  | UB - UV (with BIT) | [11 empty] | * This staus is not applicable in 40/40L, L4.
|  | Detector Configuration Selection |  |  |  | 1 - Factory Default
Configure the detector by selecting options from the drop down below. |  |  |  | BIT = Built in Test |  | * - Status of relay after successful startup
|  | Detector Type: | LB - UV/IR (with BIT) | Maximum Operation Temperature | 1 | Enclosure Material |  |  | S
|  | Wiring Option: | 1 | 1 - 75°C |  | A - Aluminum
|  | Max. Operation Temp.: | 1 - 75°C | 2 - 85°C |  | S - Stainless Steel
|  | Conduit Size: | 2 - 3/4" | Conduit Size | 2 | Listing
|  | Enclosure: | S - Stainless Steel | 1 - M25 |  | F - Factory Mutual (FM)
|  | Listing: | F - Factory Mutual (FM) | 2 - 3/4" |  | C - ATEX / IECEx
|  | Factory Programming Selection |  | Factory Programming Descriptions
|  | Alarm Delay: | A - (Anti-Flare) | Alarm Delay |  | Heated Optics
|  | Sensitivity: | 15m (50ft.) | 0 - No Delay | F | Auto - Automatically controlled
|  | Heated Optics: | Auto - Automatically controlled | A - (Anti-Flare) |  | Off - Heater always off
|  | Heat On Temp | 5°C (41°F) | 3 - Seconds |  | On - Heater always on
5 - Seconds
|  |  |  | 10 - Seconds |  | * In Auto mode, the default 'Heat On' setting is 5°C or 41°F.
|  | * Other Functions: |  | 15 - Seconds |  | Heating stops at 15°C or 59°F above the 'Heat On' temperature.
1. |  | Alarm Latching: | No | 20 - Seconds |  | You can also define the 'Heat On' temperature (between 0°C and
2. |  | Aux. Relay on Warning: | No | 30 - Seconds |  | 50°C or 32°F and 122°F),below which the window will also be heated.
3. |  | Enable "Automatic BIT": | Yes
4. |  | Alarm On "Manual BIT": | No | Sensitivity
5. |  | Aux. on "Manual BIT": | No | 15m (50ft.) |  |  |  | Gas Detectors USA
6. |  | Aux./Acc. Relay as EOL: | No |  |  |  |  | 4339 Stacy LN Seabrook, TX 77586
Phone: 832-615-3588
| * When blanked out the factory default option cannot be changed |  |  |  |  | Yes |  | E-Mail: orders@GasDetectorsUSA.com
|  | Current Detector Model #: | 40/40LB-112SF |  |  | No |  | Web: www.GasdetectorsUSA.com
Note 1: Macros must be enabled for all features of the spreadsheet to work properly
Note 2: Before configuring a new detector is is recommended you reset the sheet to the default settings using the "Reset Sheet" button located in the lower right corner.
5°C (41°F)
10°C (50°F)
15°C (59°F)
20°C (68°F)
25°C (77°F)
30°C (86°F)
Zoom to Fit
Reset Sheet
E-Mail Sheet